## Slide 1
CPT-based Multifunctional Grid-Tied Inverter with Type II Controller
Team G2 Power
Tiago Davi Curi Busarello, José de Arimatéia O. Filho, Alex Ferreira Silva, Paulo Fernando Silva, Helmo Kelis Morales Paredes
Notes: Deixei título em negrito

## Slide 2: Introduction and motivation
Prof. Tiago Davi Curi Busarello
Distributed Energy Resources (DERs) are becoming increasingly common in modern electric power systems.
1547 - IEEE Standard for Interconnection and Interoperability of Distributed Energy Resources with associated Electric Power Systems Interfaces

## Slide 3: Introduction and motivation
Prof. Tiago Davi Curi Busarello

## Slide 4: Introduction and motivation
Prof. Tiago Davi Curi Busarello
Multifunctional inverter (ancillary services) appears as an attractive solution to the new updates of connecting DERs to the electric power system
Fig. 1: Effects of active and reactive power on voltage change at diferente X/R ratios.
Notes: Modifiquei legenda

## Slide 5: Proposed System and Control
Prof. Tiago Davi Curi Busarello
The point is: multifunciotnal converters (MFGTI) will are a reality in power systems. And it will be much more
Develop a multifunctional inverter to address the IEEE1547-2023
Even though the IEEE1547 does not talk about current Harmonic compensation, the proposed inverter is already ready for such a compensation.
Use of the Conservative Power Theory to compute power quantities of loads.
7 modes of operation.
Use just one current controller for all modes of operation, differently from switchable controller strategies in inverters with ancillary services.
Notes: Inseri MFGTI

## Slide 6: Proposed System and Control
Prof. Tiago Davi Curi Busarello
Fig. 2: (a) Overview of MFGTI, (b) block control strategy.

## Slide 7: Proposed System and Control
Prof. Tiago Davi Curi Busarello
Transfer function: Type-II current controller ()
Coefficients
where:
Design current controller
Type-II current controller ()
pole at the origin and single zero–pole pairs
enhances robustness against load variations
external disturbances
efficient and relatively simple solution
alternative controller in MFGTI
Notes: Structurally, this compensator combines a pole at the origin, which provides the integral action required to eliminate steady-state error, with a pole-zero pair that introduces phase lead [11]. The integral action ensures accurate tracking even under persistent disturbances, while the phase lead component counteracts the inherent delays of the plant, improving phase margin and enabling faster and more stable dynamic response [12].

## Slide 8: Modes of Operation
Prof. Tiago Davi Curi Busarello
Mode 1: Injecting Active Power
Mode 2: Full Shunt Power Filter
Mode 3: Reactive Power Compensation (Statcom)
Mode 4: Harmonic compenstation
Mode 5 Active and Reactive power Injection
Mode 6: Active power consumption and reative power injection
Mode 7: stand-by
More modes could be added (combination of them)

## Slide 9: Model – Power Structure (TyphoonSim® 2025.2)
Prof. Tiago Davi Curi Busarello
NLL
MFGTI
Power grid
Fig. 3: Power Structure of MFGTI in TyphoonSim® 2025.2.
Notes: Fig. 3: Power Structure of MFGTI in TyphoonSim® 2025.2

## Slide 10: Model – Reference Generators (TyphoonSim® 2025.2)
Prof. Tiago Davi Curi Busarello
Fig. 4: Reference Generators of MFGTI in TyphoonSim® 2025.2.
Notes: Fig. 4: Refrence Generators of MFGTI in TyphoonSim® 2025.2

## Slide 11: Model – Model Selector and Current Controller (TyphoonSim® 2025.2)
Prof. Tiago Davi Curi Busarello
Current Controller:
Mode Selector
Fig. 5: (a) Model selector; (b) current controller of MFGTI.
(a)
(b)
Notes: Fig. 5: (a) Model selector; (b) current controller of MFGTI

## Slide 12: Model – Scripts in Matlab® and Python
Prof. Tiago Davi Curi Busarello
(i) Script in Matlab
(ii) Script in Python

## Slide 13: Model – Mode Selector and Current Controller (TyphoonSim 2025.2)
Prof. Tiago Davi Curi Busarello
Trade-off between filter size and power quality
Fig. 6: (a) current reference and MFGTI current; (b) grid current, grid voltage/10; (c) error.

## Slide 14: Extension of our model
Prof. Tiago Davi Curi Busarello
Fig. 7: Extension of the proposed model.

## Slide 15: Extension of our model
Prof. Tiago Davi Curi Busarello
Fig. 8: Results from the extension of the proposed model.

## Slide 16: Extension of our model
Prof. Tiago Davi Curi Busarello
Fig. 8: Overview of the experimental MFGTI set-up.
Complete demonstration: https://youtu.be/aGTE193b3e0

## Slide 17: Freely available files
Prof. Tiago Davi Curi Busarello
https://busarello.prof.ufsc.br/challenge.html
https://github.com/TeamG2Power

## Slide 18: Conclusions
Prof. Tiago Davi Curi Busarello
The proposed multifunctional inverter is an attractive solution for DER to address the new requirements of IEEE1547.
Using only one controller for all modes of operation proved to be a good choice instead of using switchable controller when performing ancillary services.
The CPT could compute accurately the power quantities for the operation modes.
The proposed inverter is ready to inject the required active and reactive power for contributing to regulate voltage and frequency of the point of common coupling.

## Slide 19
Thank you!!
Questions?
tiago.busarello@ufsc.br